## Kavuthu- Unpriced
PROPOSED COMPLETION OF POST HARVESTING FACILITY (COLDROOMS AND PACK HOUSE) AT KAVUTHU IN MAKUENI COUNTY.- PHASE 2
ITEM | DESCRIPTION | QNTY | UNIT | RATE | AMOUNT
1.0 MAIN HOUSE -REPAIRS AND ALTERATIONS
Roof Works
0
| Rain Water Goods |  |  |  | 0
A | 250mm diameter, outlets including making good the existing gutter. | 10 | NO
B | 250mm diameter support brackets | 50 | NO
C | 250mm diameter joint unions | 24 | NO
D | Ditto for outlets | 6 | NO
E | Ditto but elbow | 4 | NO
F | 200mm diameter heavy duty PVC rain water downpipe fixed to wall with holder clips. | 72 | LM
G | Extra over ditto for swan neck | 6 | NO
I | Ditto for horse shoe | 6 | NO
Painting to steel Gutters
Prepare and apply three coats of gloss paint to:
J | General surfaces of metal Gutters (both inside and outside). | 50 | LM
K | Ditto but super strong bonding leak-proof sealant to joints to approval. | 50 | LM
L | Ditto but, painting to Metal grill surfaces. | 36 | SM
Ventilation Appliances.
M | Supply and install stainless steel rotating roof cyclones ventilators, 500mm diameter, aluminium construction, powder coated finish complete with weather proof flashing and fasteners, including all necessary accessories. | 4 | NO
Total carried to Collection
ITEM | DESCRIPTION | QNTY | UNIT | RATE | AMOUNT
Wash Hand Basins
A | Supply and fix stainless steel double sink complete with taps ,mansory stand and concrete top, finished with white glazed tiles , including drainage works and connection to the existing drainage system.(m/s). | 2 | NO
Floor Finishes
C | Carefully,Hack out the cracked floor,appro. 335 sm, including preparation and making good to receive new floor finish and dispose all the debris away from site as directed by the P.M | 420 | SM
Cement and sand backing (1:3) finished as described
D | 15mm thick cement and sand screed finished hard with wood float to receive Epoxy finish (m/s) | 420 | SM
Terrazzo Floor Finish
E | Supply and apply 25mm thick polished terrazzo finish, I cluding grinding and regular partens as per Engineers Instructions and approval | 420 | SM
Total carried to Collection
COLLECTION
Total Brought forward from Pg 01
Total Brought forward from Pg 02 Above
TOTAL FOR REPAIRS AND ALTERATIONS TO THE EXISTING BUILDING CARRIED TO SUMMARY PAGE.
2.0 EQUIPING
ITEM | DESCRIPTION | QNTY | UNIT | RATE | AMOUNT
Sorting Tables
A | Supply and install stainless steel soarting tables sizes 2400mmx1200mmx900mm high, with drain pipes to allow connction to the existing drainage system. | 3 | NO
Storage Racks
B | Supply and install 5 tier, stainless steel storage racks of size 2000mmx650mmx11675mm high, Each shelf shall be constructed in stainless steel sheets 3mm thick, with a 50mm up stand all round. Thw whole unit shall be substantially constructed such that shelves are evenly distributed, the frame shall be stainless steel 32mmx3mm thick, with adjustable sanitary feet. | 1 | NO
TOTAL FOR EQUIPING CARRIED TO SUMMARY PAGE.
ELECTRICAL INSTALLATION - KAVUTHU COLDROOM
ELECTRICAL WORKS
ITEM | DESCRIPTION | QTY | UNIT | RATE (Kshs) | AMOUNT (Kshs)
1 | 16mm sq. 4 core CU/XLPE/PVC as EA cables or similar approved equivalent | 10 | LM
1.2 | Lockable Meter box measuring 24 inch by 24 inch complete with all necesary accessories | 1 | NO
Total For Electrical Instalation Works Carried to Main Summary
EQUIPPING AND DISTRIBUTION OF KAVUTHU COLDROOM BOREHOLE IN MBITINI WARD BILL OF QUANTITIES
ALL PRICES ARE INCLUSIVE OF TRANSPORT, LABOUR COSTS, PROFITS, OVERHEADS & VAT
BILL OF QUANTITIES
Item | Description | Unit | Qty | Rate (Ksh) | Amount (Kshs)
BILL 1) BOREHOLE PUMP AND ACCESSORIES
| ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
NO. |  |  |  |  | KSHS.
Supply, transport, Install and Test materials to equip Kavuthu coldroom Borehole under supervision of client's engineer. The rate is deemed to include supply, installation and testing of all material for equiping Kavuthu coldroom BH to supervising engineeer satisfaction.
PUMP, MOTOR & SUNVERTER
1.1 | Supply, Deliver, Install and Test an hybrid Submersible Multistage Centrifugal Pump Set of Duty Point: - 8.5 m3/hr at a Total Head of 205 meters and 7.5 kw motor. The pump Efficiency at duty point should not be less than 55%. The pump Impellers should be of Stainless Steel. Provide Copies of Pump Characteristic /Performance Curves (Brochures). Install DS 8-50 or equivalent as approved by the Supervising Engineer | Set | 1
1.2 | Supply, deliver and install a 3 phase, 415Vac, approved pump control panel incorporating: - i) 7.5 kW S/D Starter, c/w appropriate rating contactors, i.e. Main, Star & Delta ii) Appropriate rating overload relay as iii)Panel door mounted ammeter, >200Amps , c/w CTs iv) panel door mounted voltmeter, 0 - 500Vac, c/w voltage selector switch v) Water Level Relay, with sensitivity sensor in % vi) Phase failure relay, c/w max/min control vii) Indicator lamps: Green - run; Red - trip; Yellow - low water viii) Hand/auto selector switch, Start/stop push button ix) ADD OPTION - MA (ABOVE 7.5 KW) x) 3phase integral circuit breaker, >250Amps xi) Auxiliary circuit protective fuses, 3No xii) fully wired and labelled; provide 2 copies of schematic and control wiring diagram | Unit | 1 |  | 0
1.3 | 24 x 24 Meter box to engineers specifications, fully equipped as shall be instucted; 125A MCCB | Item | 1
1.4 | Circuit Disconnect Switch, 63Amps | No. | 1
1.5 | Three phase Borehole Drop submersible Cable, 6 mm2 X 4 core | LM | 180
1.6 | Londex Sensor Cable, Twin, Double Insulated, 1.5 mm2 X 2 core | LM | 180
1.7 | UG armored Cable, 6.0 mm2 X 4 core | LM | 65
1.8 | UG armored Sensor Cable, 1.5 mm2 X 2 core | LM | 65
1.9 | Supply 1" G.I pipe class B to use as conduit for cables and to be covered with concrete | LM | 6
1.1 | Cover the cables using concrete class 20 mix 1:2:4 as instructed by supervising engineer | CM | 1
1.11 | UPVC Conduit, HG, 1” Ø 6m lengths | No. | 5
1.12 | Cable Glands, 25mmL | No. | 4
1.13 | Cable Glands, 20mmL | No. | 2
1.14 | Splicing Kit, Medium Packet | No. | 1
1.15 | Cable Ties, Large Packet, Manila | No. | 2
1.16 | Insulating Tapes, Large | No. | 20
SUBMERSIBLE PIPES & BOREHOLE CHAMBER FITTINGS
1.17 | Supply, Install and Test strong non corroding uPVC Borehole Pipes maximum allowable pressure 26 bar, 2" Ø X 3m | No. | 62
1.18 | Adaptor Set, 1.25"Ø | Set | 1
1.19 | Cutting of the borehole casings and joining the steel borehole Cover, c/w Fittings | Item | 1
1.2 | UPVC Pipes, ¾” Ø X 6m, Class ‘D’ | No. | 31
1.21 | Master Water Meter, 2” multi-jet, Brass Body, Screw Type, Class B, PN20, c/w Fittings | No. | 1
1.22 | Non return valve 2" | No. | 1
1.23 | Construction of a reinforced concrete cover levelled at the ground level | No. | 1
1.24 | Replacement and reinstallation of cabro paving blocks section around the borehole | SM | 10
1.25 | 2" G.I pipe at the borehole c/w fittings, threading, cutting, welding and anchoring | LM | 18
1.26 | Supply and install DC enclosure complete with inline 1100VDC fused isolator | NO | 2
1.27 | Supply and install Automatic Voltage Stabilizer (AVS) | NO | 1
1.28 | Allow for electrical wiring, system earthing, lightening arrestor c/w surge protector and copper strip and balance of system | Lot | 1
1.29 | Allow for installation sundries as Hg flex conduit, cable ties, MC4 Connectors, cable lugs cable clips and all necessary assortment | Lot | 1
| Sub Total Carried for collection in summary page |  |  | KSH.
BILL 2) PIPELINE NETWORK
| ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
NO. |  |  |  |  | KSHS.
2.1 | Clearing site and excavation to pipe invert level as per engineer's specifications (trench minimum depth 600 mm), lay, test pipeline and backfill to ground level for item 2.2 | LM | 100
2.2 | Supply, deliver, install and test O/D 63 mm (2") HDPE pipes PN12.5 as per KS ISO 4427:2007 joint with connectors. To be laid in the same trench as item 2.1 above | LM | 100
STORAGE TANK
2.3 | Fabricate and install 10 m high tank platform to hold 1No. 2 CM Plastic water tanks. Use 4 No 40 x 40 x 3 mm SHS | No | 1
2.4 | Supply, install and test 1 No. 2,000 Ltrs double layer plastic water tanks on item 2.3 above. | No | 1
Booster pump
2.5 | Supply a booster pump to deliver 3 m3 at 15 m head | No | 1
2.6 | provide for a steel lockable chamber for housing booster pump | No | 1
2.7 | Provide for electrical wiring c/w conduit and switch | Item | 1
2.8 | Supply, deliver, install and test O/D 32 mm (1") PPR pipes from outlet to elevated tank | LM | 100
Plumbing works
2.9 | Supply, deliver, lay/ fit/ anchor as directed and test 1" pipeline GI Pipe class B with respective adaptors for inlet | LM | 18
2.1 | 63mm GI pipes (2") class B with sockets for outlet | LM | 12
2.11 | 63 mm (2") G.I equal tee | No. | 1
2.12 | 63 mm Pegler gate valve or equivalent approved | No. | 1
2.13 | Supply, instal and test 50mm Pegler gate valve or equivalent approved | No. | 2
2.14 | 63 mm x 50 mm (1.5") reducer | No. | 2
2.15 | Supply, deliver, install and test O/D 50 mm (1.5") PPR pipes from outlet to existing tanks and tanks above the abulition c/w fittings and anchoring | LM | 200
2.16 | Construct a standard water point with lockable tap as instructed | No. | 1
2.17 | Rehabilitation of gutter system including installaton of a steel bar to hold gutter system | Item | 1
2.18 | Supply PVC Nylon Braided 3/4″ Inch Heavy Duty Industrial Grade Garden Hose Flexible Water Pipe | No. | 1
| Sub Total Carried for collection in summary page |  |  | KShs.
BILL 3) VALVE CHAMBER
No. | ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
|  |  |  | KShs. | KShs.
Supply materials and provide personnel to construct a gate valve chamber (as in the attached drawing)
3.1 | Cut the spoil upto 300mm below g.l. over the borehole chamber area and remove all vegetable soil to temporary spoil heap. | M3 | 0.3
3.2 | Excavate foundation from stripped level over the borehole chamber site to depth n.e. 0.6m deep 300 mm wide and dispose soil as directed | M3 | 1
3.3 | Mass concrete mix 1:4:8: in 50mm concrete slab | M3 | 0.1
3.4 | 225mm thick dressed quarry stone walling | M² | 5
3.5 | Provide and instal a lockable double steel Cover c/w padlock | No. | 1
3.6 | EXTERNAL PLASTER - 20mm thick 1:2 cement sand to exterior face of the valve chamber wall | M² | 4
Sub total carried for collection in the summary page
BILL 4) | CONTINGENCY | UNIT | QTY | RATE | AMOUNT
|  |  |  | KSHS. | KSHS.
4.1 | Allow a Provisional sum of Kshs 150,000 for Contingencies to be expended by project manager
Sub Total carried for collection in the summary page
BILL | GRAND SUMMARY | UNIT | QTY | RATE | AMOUNT
KSHS
1 | BOREHOLE PUMP AND ACCESSORIES
#REF!
2 | PIPELINE NETWORK
3 | VALVE CHAMBER
4 | CONTINGENCY
TOTAL FOR WATER SUPPLY AND DISTRIBUTIONCARRIED TO MAIN SUMMARY
SUPPLY AND INSTALLATION OF FIRE FIGHTING EQUIPMENT
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
A | Purchase and supply of Occupational First Aid Kits | NO | 1
B | Purchase and supply of Fire Balls [4 kg] | NO | 2
C | Purchase and supply of Portable Extinguishers Co2 5 Kgs | NO | 1
D | Servicing Portable Fire Extinguishers Co2 5 Kgs | NO | 4
E | Fabricate, Supply and Install a fire assembly point, signage, comprising of mild steel plate G14, 50mmx5mmx2.5mm steel tube fixed firmly to the Ground with concrete suround, including all excavations and Painting works to Approval | NO | 1
F | Supply of fire signage-exit routes (as per structural design/layout) Luminous | NO | 2
G | Ditto but Non Luminous | NO | 4
H | Purchase and installation of Hose reel connectors complete with connectors and accessories | LM | 30
I | Purchase installation and testing High pressure Booster Pump-complete set | NO | 1
Sub -Total 1
Provisional sums
J | Allow for provisional sum of ten thousand Kenya Shillings for relocation of installed fire extinguishers and alarm bells |  | SUM
K | Design and supply Fire action plans and display appropriately |  | SUM
L | Design and display an architectural emergency response plan for the premises and display appropriately |  | SUM
M | Allow for provisional sum of Kenya shillings ten thousand for end use training for operating extinguishers, fire safety, evacuation procedures and means of escape |  | SUM
TOTAL CARRIED TO MAIN SUMMARY
SUMMARY PAGE
ITEM | SECTION DETAILS |  |  |  | AMOUNT
A | REPAIRS AND ALTERATIONS TO PACKHOUSE
B | EQUIPING
C | ELECTRICAL WORKS TO PACK HOUSE
D | WATER SUPPLY, STORAGE AND DISTRIBUTION
E | FIRE FIGHTING EQUIPMENT
TOTAL CARRIED TO GRAND SUMMARY.
ITEM | DESCRIPTION | QNTY | UNIT | RATE | AMOUNT
ELEMENT NO.7
PRIME COST & PROVISIONAL SUMS
A | Provide a Provisional Sum of Kenya Shillings Two Hundred Thousand ( Kshs 200,000.00) for Supply of office furniture and Equipment. |  | SUM |  | 200000
B | Provide a Provisional Sum of Kenya Shillings One Hundred Thousand ( Kshs 100,000.00) for Project Management Committee (PMC). |  | SUM |  | 100000
C | Provide a Provisional Sum of Kenya Shillings Seventy Thousand Only (Kshs 72,000.00) for Monitoring and Evaluation (M&E). |  | SUM |  | 72000
D | Provide a Provisional Sum of Kenya Shillings Seventy Two Thousand Only (Kshs 72,000.00) for Community Outreach. |  | SUM |  | 72000
E | Provide a Provisional Sum of Kenya Shillings One Hundred and Fifty Thousand Only (Kshs 150,000.00) for Project Technical Supervision, |  | SUM |  | 150000
F | Provide a Provisional Sum of Kenya Shillings One Hundred Thousand (Kshs 100,000.00) for Contigency Sums to be deducted in whole or in part at the discretion of the Project Manager. |  | SUM |  | 100000
| PRIME COST & PROVISIONAL SUMS CARRIED TO GRAND SUMMARY |  |  |  | 694000
ITEM | SECTION DETAILS |  |  |  | AMOUNT
GRAND SUMMARY
A | PRELIMINARIES
B | COMPLETION WORKS TO PACKHOUSE
Sub-Total 1
C | Public Procurement Capacity Building Levy order 2023 which is 0.03% of the total cost before tax persuant to PPRA Circular No. 1 of 2024.
ADD 16% VAT
Sub-Total 2
D | PRIME COST & PROVISIONAL SUMS |  |  |  | 694000
GRAND TOTAL CARRIED TO FORM OF TENDER.
AMOUNT IN WORDS:
DATE: